## Condenser Design
Inputs |  | Units | Error ?
Location of Steam.dll | C:\STEAM\STEAM.DLL
Wet steam inlet temperature | 37 | degree C
Steam quality | 0.95
Cooling water inlet temperature | 7 | degree C
Cooling water inlet pressure | 1.2 | bar
Cooling water outlet temperature | 22 | degree C
Cooling water outlet pressure | 1.013 | bar
Steam mass flow | 15000 | kg/h
Cooling water speed | 1.5 | m/s
Outputs
Wet steam pressure | #NAME? | bar | #NAME?
Enthalpy of steam at inlet | #NAME? | kJ/kg | #NAME?
Enthropy of condensate | #NAME? | kJ/kg | #NAME?
Rejected heat/hour | #NAME? | kJ/h
Rejected heat/second | #NAME? | kJ/s = kW
Enthalpy of water at inlet | #NAME? | kJ/kg | #NAME?
Enthalpy of water at outlet | #NAME? | kJ/kg | #NAME?
Water mass flow | #NAME? | kg/h | #NAME?
The overall heat tranfer coefficient can be calculated according to BEAMA or HEI standards.
BEAMA : British Electrical and Allied Manufacturers Association
BEAMA publication on the recomended practice for design of surface type steam condenser
HEI : Heat Exchanger Institute
HEI standards for steam surface condensers
Outputs |  | Unit
Heat transfer coeff.(BEAMA) | 2.9523 | kW/m2,K
Logarithmic mean temp. diff. | 49.8289 | degree K
Required area | #NAME? | m2 | #NAME?
If we use the less conservative HEI method we obtain the following:
Outputs |  | Unit
Heat transfer coeff.(HEI) | 3.6099 | kW/m2,K
Required area | #NAME? | m2 | #NAME?
This MS EXCEL document shows how the DLL version of Steam
Properties can be used for condenser design.
A surface condenser is required to deal with 15 000 kg/h wet steam.
Wet steam temperature is 37 C and enters the condenser with 0.95
quality (dryness fraction is 0.95). The water used for cooling has the
following data:
-inlet pressure 1.20 bar, inlet temperature 7 C
-outlet pressure 1.013 bar, outlet temperature 22 C
Calculate the flow rate of cooling water and tube surface of the
condenser. Assume that the cooling water velocity through tubes is
1.5 m/s
Note:
1-It is assumed (by running dllsetup.exe prior to start of EXCEL) that
the units are set as following:
Pressure(bar), Temperature(C), Enthalpy(KJ/Kg), Entropy(KJ/Kg,K),
Specific Volume (m3/Kg)
2-In case of using 32-bit version of MS EXCEL use steam32.dll instead
of steam.dll
3-Adjust the content of cell "LocationOfDLL" to appropriate value
Taftan Data
Nydala Torget 2, Box 23538
S-20045, Malmo,
Sweden
Fax: +46 70 614 8730
Internet: support@taftan.com
If you want to know more about "Taftan Data" or other software developed by this company please visit our website:
http://www.taftan.com